## Sheet1
Le Grand Community Services District WWTF |  |  |  |  | Month: | 2024-12-01
MRP NO. 97-053 Influent and Effluent Monitoring Data
BOD Effluent Sample Location: |  | Outlet Of Pond # 4
| Influent Monitoring |  | Effluent Monitoring
| BOD | Settleable Solids | Flow | BOD | Settleable Solids | pH | Electrical Conductivity
Unit | mg/l | ml/l | mgd | mg/l | ml/l | pH Units | µmhos/cm
Frequency | Monthly | Monthly | Daily | Monthly | Monthly | Monthly | Monthly
Type | 8-hr composite | 8-hr Comosite | Continuous | 8-hr Composite | Grab | Grab | Grab
Date/1 |  |  | 0.09
2 |  |  | 0.065
3 |  |  | 0.085
4 |  |  | 0.082
5 |  |  | 0.097 |  |  | 7.64 | 810
6 |  |  | 0.073
7 |  |  | 0.085
8 |  |  | 0.087
9 |  |  | 0.104
10 |  |  | 0.133 |  |  | 7.22 | 822
11 |  |  | 0.052
12 |  |  | 0.085
13 |  |  | 0.085
14 |  |  | 0.087
15 |  |  | 0.104
16 |  |  | 0.133
17 |  |  | 0.052 |  |  | 7.34 | 824
18 |  |  | 0.081
19 |  |  | 0.096
20 |  |  | 0.097
21 |  |  | 0.082
22 |  |  | 0.081
23 |  |  | 0.093 |  |  | 7.34 | 846
24 |  |  | 0.08
25 |  |  | 0.066
26 |  |  | 0.089
27 |  |  | 0.071
28 |  |  | 0.097
29 |  |  | 0.068
30 |  |  | 0.076 |  |  | 7.41 | 824
31 |  |  | 0.091
Average |  |  | 0.086032 | 30 | >0.5 | 7.3275 | 829
Minimum |  |  | 0.052 | 30 | >0.5 | 7.22 | 822
Maximum |  |  | 0.133 | 30 | >0.5 | 7.41 | 846
Required Limit |  |  | 0.35 | 40/80 | .2/.5 | 6.9-9.5 | 825.8333
|  |  | 0.086032 |  |  | 7.3796 | 810
|  |  | 0.052 |  |  | 7.22 | 846
|  |  | 0.133 |  |  | 7.64

## Sheet2
Le Grand Community Services District WWTF |  |  |  |  | Month: | January
MRP No. 97-053 Weekly Pond Monitoring Data |  |  |  |  | Year: | 2024
Pond Monitoring Information
Week 1 | Date | Time | Additional Notes:
1 |  | 8-9 A.M.
2 |  | 8-9 A.M.
3 |  | 8-9 A.M.
4 |  | 8-9 A.M.
5 |  | 8-9 A.M.
| DO | pH | Freeboard | Pond Monitoring
Unit | mg/l | pH Units | Observation
Type | Grab | Grab | Grab
Pond 1 |  |  |  | Week 1:
Week/ 1 |  |  | 2'
2 |  |  | 2'
3 |  |  | 2'
4 |  |  | 2'
5
Pond 2
Week/ 1 |  |  | 2' | Week 2:
2 |  |  | 2'
3 |  |  | 2'
4 |  |  | 2'
5
Pond 3
Week/ 1 |  |  | 2'
2 |  |  | 2' | Week 3:
3 |  |  | 2'
4 |  |  | 2'
5
Pond 4
Week/ 1 | Empty | Empty
2 | Empty | Empty
3 | Empty | Empty |  | Week 4:
4 | Empty | Empty
5
Pond 5
Week/ 1 | Empty | Empty
2 | Empty | Empty
3 | Empty | Empty |  | Week 5:
4 | Empty | Empty
5

## Sheet3
Le Grand Community Services District WWTF |  |  |  |  | Month:
MRP No. 97-053 Triennially Water Supply Monitoring Data |  |  |  |  | Year:
*This data is to be submitted in addition to the Annual and Monthly Monitoring Data
Triennial Water Supply Monitoring Information
Sample Date | Time | Additional Notes:
Well 1a
Well 2
Well 4
Constituent |  | Unit | Well 1A | Well 4
Conductivity |  | umhos/cm
Total Dissolved Solids |  | mg/l
Calcium |  | mg/l
Magnesium |  | mg/l
Sodium |  | mg/l
Potassium |  | mg/l
Total Alkalinity |  | mg/l
OH Alkalinity |  | mg/l
CO3 Alkalinity |  | mg/l
HCO3 Alkalinity |  | mg/l
Sulfate |  | mg/l
Chloride |  | mg/l
Fluoride |  | mg/l
Iron |  | ug/l
Total Phosphorus |  | mg/l

## Sheet4
Le Grand Community Services District WWTF |  |  |  | Monthly:
MRP No. 97-053 Yearly Effluent Monitoring Data |  |  |  | Year:
* This data is to be submitted in addition to the Monthly Monitoring Information
Annual Effluent Monitoring Information
Sample Date | Time | Additional Notes:
Constituent |  | Unit | Result
Nitrate as N |  | mg/l
Total Kjedldahl Nitrogen |  | mg/l
Calcium |  | mg/l
Magnesium |  | mg/l
Sodium |  | mg/l
Potassium |  | mg/l
Total Alkalinity |  | mg/l
OH Hydroxide Alkalinity |  | mg/l
CO3 Carbonate Alkalinity |  | mg/l
HCO3 Bicarbonate Alkalinity |  | mg/l
Sulfate |  | mg/l
Chloride |  | mg/l
Flouride |  | mg/l
Iron |  | mg/l
Total Phosphorus |  | mg/l